| KW | Volts | Phase | Total Amps (1) | CFM | Approximate Air Temperature Rise oF (oC) | Motor Data |  |  | Weight lb (kg) | Catalog Number |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | HP | RPM | Voltage |  |  |  |
| 3.2 | 480 | 3 | 4.7 | 450 | 22 (12) | 1/25 | 1050 | 208/240 | 75 (34) | HX-928C03200UA |  |
| 4.8 | 480 | 3 | 6.6 | 450 | 34 (10) | 1/25 | 1050 | 208/240 | 75 (34) | HX-928C04800UA |  |
| 5 | 208 | 1 | 24.9 | 450 | 36 (20) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C05000CA |  |
|  | 208 | 3 | 14.7 | 450 | 36 (20) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C05000DA |  |
|  | 240 | 1 | 21.7 | 450 | 36 (20) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C05000JA |  |
|  | 240 | 3 | 12.9 | 450 | 36 (20) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C05000KA |  |
| 6.4 | 480 | 3 | 8.6 | 600 | 34 (19) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C06400UA |  |
| 7.5 | 208 | 3 | 21.7 | 600 | 40 (22) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C07500DA |  |
|  | 240 | 1 | 32.1 | 600 | 40 (22) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C07500JA |  |
|  | 240 | 3 | 18.9 | 600 | 40 (22) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C07500KA |  |
| 9.6 | 480 | 3 | 12.5 | 1200 | 25 (14) | 1/6 | 1140 | 208/240 | 75 (34) | HX-928C09600UA |  |
| 10 | 208 | 3 | 28.6 | 750 | 41 (23) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C10000DA |  |
|  | 240 | 1 | 42.5 | 750 | 41 (23) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C10000JA |  |
|  | 240 | 3 | 24.9 | 750 | 41 (23) | 1/20 | 1050 | 208/240 | 75 (34) | HX-928C10000KA |  |
| 12.8 | 480 | 3 | 16.3 | 1200 | 34 (19) | 1/6 | 1140 | 208/240 | 100 (48) | HX-928C12800UA |  |
| 15 | 208 | 3 | 43.4 | 1200 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C15000DA |  |
|  | 240 | 1 | 64.3 | 1200 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C15000JA |  |
|  | 240 | 3 | 37.9 | 1200 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C15000KA |  |
| 16 | 480 | 3 | 20.2 | 1600 | 32 (18) | 1/6 | 1140 | 208/240 | 100 (48) | HX-928C16000UA |  |
| 19.2 | 480 | 3 | 24 | 1600 | 38 (21) | 1/6 | 1140 | 208/240 | 100 (48) | HX-928C19200UA |  |
| 20 | 208 | 3 | 57.3 | 1600 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C20000DA |  |
|  | 240 | 1 | 85.1 | 1600 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C20000JA |  |
|  | 240 | 3 | 49.9 | 1600 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C20000KA |  |
| 25 | 208 | 3 | 71.2 | 2000 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C25000DA |  |
|  | 240 | 1 | 106 | 2000 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C25000JA |  |
|  | 240 | 3 | 61.9 | 2000 | 40 (22) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C25000KA |  |
| 30 | 208 | 3 | 85.1 | 2300 | 41 (23) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C30000CA |  |
|  | 240 | 1 | 126.8 | 2300 | 41 (23) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C30000JA |  |
|  | 240 | 3 | 74 | 2300 | 41 (23) | 1/8 | 1140 | 208/240 | 100 (48) | HX-928C30000KA |  |

(1) Total Amps = Heating element amps and motor amps.

Other voltages available.  Consult factory.

Only available with almond finish.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |
| D1 | Disconnect Switch 40A, 600V, 3-Pole |  |
| D2 | Disconnect Switch 80A, 600V, 3-Pole |  |
| R1 | 24V Relay |  |
| R2 | 24V Relay with Transformer |  |
| X | 120V Control, fused secondary and grounded |  |

Field-Installed Options

(shipped loose for field installation into heater)

| Catalog Number | Description |  |  |
| --- | --- | --- | --- |
| 928-124521 | Single Cone Diffuser | 5-10 KW |  |
| 928-124522 | Single Cone Diffuser | 15-30 KW |  |
| 928-124523 | Triple Cone Diffuser | 5-10 KW |  |
| 928-124524 | Triple Cone Diffuser | 15-30 KW |  |
| 928-124525 | Jet Cone Diffuser | 5-10 KW |  |
| 928-124526 | Jet Cone Diffuser | 15-30 KW |  |
| 928-124527 | 24V Relay Kit |  |  |
| 928-124528 | 24V Relay Kit with Transformer-208V |  |  |
| 928-124529 | 24V Relay Kit with Transformer-240V |  |  |

Without Cone	Single Cone	Triple Cone	Jet Cone

Maximum Mounting Height

| KW | Without Cone |  | Single Cone |  | Triple Cone |  | Jet Cone |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | H | S | H | S | H | S | H | S |
|  | Ft (m) | Ft (m) | Ft (m) | Ft (m) | Ft (m) | Ft (m) | Ft (m) | Ft (m) |
| 5-10 | 12 (4) | 19 (6) | 8 (3) | 22 (7) | 10 (3) | 31 (10) | 16 (5) | 20 (6) |
| 15-30 | 18 (6) | 20 (9) | 10 (4) | 33 (10) | 14 (4) | 43 (13) | 22 (7) | 26 (9) |

Support Brackets

| Model (without cone) | A | B | C |
| --- | --- | --- | --- |
|  | In. (mm) | In. (mm) | In. (mm) |
| 5-10 KW | 23-1/8 (587) | 8 (203) | 6-15/16 (176) |
| 15-30 KW | 30-1/4 (768) | 12-3/16 (310) | 6-11/16 (170) |

Architect’s and Engineer’s Specifications

The specified heating equipment shall include an electric, fan-forced air unit heater suitable for space heating as manufactured by HEATREX. The vertical unit heater shall be designed for mounting in the vertical position. Heaters shall be third party approved to CSA standards. Reference: UL standard 2021.

Heating Housing shall be made from 18 gauge steel. Cabinet finish shall be an almond epoxy/polyester powder paint. Mounting support brackets shall be furnished as shown.

Heater Elements shall be finned tubular and grounded for extra safety.

Motor shall be totally enclosed and thermally protected.

Fan Over-ride shall be included to purge the heater of residual heat when heater is deenergized.

Thermal Cutout shall be built-in to every heater and wired for instantaneous de-energizing of the heating elements.

Terminal Block shall be built-in to every heater for remote fan control.

Three Types of Diffuser Cones may be added for specific airflow patterns. See previous pages for the characteristics of the three optional diffuser cones: Single, Triple and Jet.

Low Voltage Relays with or without transformers are available built-in or supplied separately as kits.

Mounting for 10 kW and less: 4 threaded holes (½ –13 UNC) are provided. For 15 kW and greater: 4 support brackets are included.